# FB_Diverter Functional Specification

Version: V1.1

# 1. Document Information

| Document Name | FB_Diverter Functional Specification |
| --- | --- |
| Function Block Name | FB_Diverter |
| Project | [Project Name] |
| Library | [Library Name] |
| Version | V1.1 |
| Author | Vijayakumar V S |
| Date | 10-Jul-2026 |
| Status | Draft for Approval |
| Approval | [Approver Name] |

# 2. Purpose

FB_Diverter controls a two-position pneumatic diverter using two feedback sensors and two digital outputs. The function block supports Manual, Bypass, Out Of Service and Automatic operation, timeout monitoring, interlock validation and fault diagnostics.

# 3. Scope

This function block controls the following components and features:

Pneumatic diverter

2 Digital Inputs

2 Digital Outputs

HMI/SCADA   Interface

Diagnostics

# 4. Functional Description

The complete operating sequence is described below:

## Initialization

Checks internal consistency, sets safe output states, and prepares to evaluate input conditions.

## Idle

Waits for a valid command to move to Way1 or Way2.

## Move to Way1

Activates OutputWay1 and starts the timeout monitor to reach FeedbackWay1.

## Move to Way2

Activates OutputWay2 and starts the timeout monitor to reach FeedbackWay2.

## Position confirmation

Validates the correct sensor is active (and the other is inactive).

## Fault handling

Detects timeouts, sensor conflicts, or permissive losses. Transitions to safe state.

## Reset

Clears latched faults if conditions are normal.

## Disable behavior

Transitions directly to the safe state.

## Safe state

All motion outputs are deactivated.

# 5. Operating Modes

| Value | Mode | Description |
| --- | --- | --- |
| 0 | Manual | Manual operation, ignores Interlock |
| 1 | Auto | Automatic operation, checks Interlock and Enable signal |
| 2 | Out Of Service | Outputs OFF .Ignore commands .State machine stopped |
| 3 | Bypass | Ignore Interlock .Still monitor safety and faults. Allow maintenance/testing. |

# 6. Command Interface

Commands are edge triggered. Executing a command requires a rising edge transition.

| Value | Command | Description |
| --- | --- | --- |
| 0 | None | No command active |
| 1 | Move Way1 | Command diverter to move to Way1 |
| 2 | Move Way2 | Command diverter to move to Way2 |
| 3 | Reset Fault | Reset active faults |

# 7. Input Signals

| Signal | Type | Description |
| --- | --- | --- |
| Enable | BOOL | Enables FB execution in Auto mode |
| FeedbackWay1 | BOOL | Sensor feedback for Way1 position |
| FeedbackWay2 | BOOL | Sensor feedback for Way2 position |
| PermissiveWay1 | BOOL | Interlock to allow motion to Way1 |
| PermissiveWay2 | BOOL | Interlock to allow motion to Way2 |
| ModeWord | WORD | Selected operating mode (0=Manual, 1=Auto, 2=OOS, 3=Bypass) |
| CommandWord | WORD | Command execution trigger |
| MoveTimeout | TIME | Timeout preset for motion supervision |

# 8. Output Signals

| Signal | Type | Description |
| --- | --- | --- |
| OutputWay1 | BOOL | Command to activate pneumatic valve for Way1 |
| OutputWay2 | BOOL | Command to activate pneumatic valve for Way2 |
| StatusWord | WORD | Bitfield containing FB status |
| FaultCode | INT | Active fault code (0 = No Fault) |

# 9. State Machine

STATE_IDLE: Awaiting commands.

STATE_MOVE_WAY1: OutputWay1 active, waiting for FeedbackWay1.

STATE_MOVE_WAY2: OutputWay2 active, waiting for FeedbackWay2.

STATE_AT_WAY1: Position confirmed at Way1.

STATE_AT_WAY2: Position confirmed at Way2.

STATE_FAULT: Error detected, outputs disabled, awaiting reset.

# 10. Sequence of Operation

Power ON
↓
Initialize position
↓
Wait for command
↓
Validate mode
↓
Validate permissives
↓
Start output
↓
Monitor timeout
↓
Confirm feedback
↓
Complete motion
↓
Ready

# 11. StatusWord Definition

| Bit | Name | Description |
| --- | --- | --- |
| 0 | Ready | Ready for commands |
| 1 | Busy | Actively firing valves (motion in progress) |
| 2 | Moving | State is MOVE_WAY1 or MOVE_WAY2 |
| 3 | At Way1 | Confirmed positioned at Way1 |
| 4 | At Way2 | Confirmed positioned at Way2 |
| 5 | Manual Active | Running in Manual mode |
| 6 | Auto Active | Running in Auto mode |
| 7 | Out Of Service | Running in OOS mode |
| 8 | Bypass Active | Running in Bypass mode |
| 15 | Fault | Active fault condition (Check FaultCode) |

# 12. Fault Handling

Fault latching: Faults remain active until a reset command is received.

Fault reset: Acknowledges and clears the latched fault if the condition is gone.

Safe output shutdown: All motion outputs deactivate upon a fault.

Motion timeout: Triggers if motion is not completed within MoveTimeout.

Sensor conflict: Triggers if both position sensors activate simultaneously.

Loss of position: Triggers if sensor feedback is lost while at position.

Invalid commands: Triggers if commands are unsupported or out of sequence.

Invalid mode: Triggers if ModeWord is out of range.

# 13. Fault Code Table

| Fault Code | Name | Description | Operator Action |
| --- | --- | --- | --- |
| 101 | Move Timeout - Way1 | Failed to reach Way1 in time | Check mechanics/sensor |
| 102 | Move Timeout - Way2 | Failed to reach Way2 in time | Check mechanics/sensor |
| 103 | Sensor Conflict | Both sensors active simultaneously | Check sensor wiring |
| 106 | Unknown Internal State | Logic entered undefined state | Reset logic |
| 107 | Enable Lost During Auto Motion | Enable dropped during Auto mode movement | Restore Enable |
| 108 | Position Lost | Sensor dropped out while holding position | Check mechanics/sensor |
| 110 | Invalid ModeWord | ModeWord is out of valid range (0-3) | Correct HMI ModeWord |
| 111 | Invalid CommandWord | CommandWord is out of valid range (0-3) | Correct HMI CommandWord |
| 114 | Move Command to Current Position (Way1) | Commanded Way1 while already at Way1 | Clear command |
| 115 | Move Command to Current Position (Way2) | Commanded Way2 while already at Way2 | Clear command |
| 120 | Unknown Position at Startup | Neither sensor active during PLC boot | Manual move required |

# 14. Timing Diagram

Command   ____|¯¯¯¯|________________
Output    ____|¯¯¯¯¯¯¯¯¯¯¯|_________
Feedback  __________|¯¯¯¯¯¯¯¯¯¯¯¯¯¯|
Timeout   ____|¯¯¯¯¯¯¯¯¯¯¯¯¯¯¯¯¯¯¯¯|
Motion    ____|¯¯¯¯¯¯¯¯¯¯¯|_________

# 15. FBD Example

+-------------------------+
          |       FB_Diverter       |
 Enable --| Enable       OutputWay1 |-- Valve1
 Fbk1   --| FbkWay1      OutputWay2 |-- Valve2
 Fbk2   --| FbkWay2      StatusWord |-- HMI_Status
 Perm1  --| PermWay1    FaultActive |-- _Fault
 Perm2  --| PermWay2                |
 Mode   --| ModeWord                |
 Cmd    --| CommandWord             |
 Time   --| MoveTimeout             |
          +-------------------------+

# 16. Design Rules

One assignment per output.

State machine architecture.

Faults are latched.

Commands are edge triggered.

Outputs are mutually exclusive.

Safe state on disable.

Timer blocks executed every scan.

No duplicate output assignments.

Follow AGI Milltech Standard.

# 17. Assumptions

Feedback sensors are mutually exclusive.

Only one command is active.

Motion timeout is configurable.

Digital outputs are fail-safe.

Exactly one position feedback shall be active during normal operation.

# 18. Future Enhancements

Output feedback

Simulation mode

Maintenance mode

Alarm history

Event logging

Remote diagnostics

# 19. Revision History

| Version | Date | Author | Description |
| --- | --- | --- | --- |
| V1.0 | 2026-07-09 | Vijayakumar V S | Initial draft |
| V1.1 | 10-Jul-2026 | Vijayakumar V S | Updated operating modes (Manual/Auto/OOS/Bypass), startup validation, and fault handling per latest codebase. |