FB_GroupStartControl Functional Specification

Version: V1.0

# 1. Document Information

| Document Name | FB_GroupStartControl Functional Specification |
| --- | --- |
| Function Block Name | FB_GroupStartControl |
| Project | [Project Name] |
| Library | [Library Name] |
| Version | V1.0 |
| Author | Vijayakumar V S |
| Date | 13-Jul-2026 |
| Status | Draft for Approval |
| Approval | [Approver Name] |

# 2. Purpose

The FB_GroupStartControl function block coordinates and executes the sequential starting. The block utilizes standard User Defined Types (UDTs) for its arrays to ensure simple, central scalability. It guarantees orderly command distribution, monitors status feedbacks, validates command structures and system parameter boundaries, handles emergency safe shutdowns, and reports comprehensive diagnostics via a packed StatusWord and numeric fault codes.

# 3. Scope

This function block manages the following features and interfaces:

Sequential control loop execution for a configured list of independent motors.

Centralized array scalability via the ArrayOfMotorWords UDT (default size: 32).

Asynchronous parameter configuration validation (one motor checking scan per plc loop).

Global system command range validation.

Individual motor operational mode assignments (Manual, Auto, Out Of Service, Bypass).

Monitored command routing and feedback evaluation with configurable timeout supervision.

Synchronous interlock permissive drop evaluation and latched fault reporting.

Operator global abort stop overrides.

Power-up cold-start reset and safe state output recovery.

# 4. Functional Description

The control system operations are organized into the following sequential segments:

## Initialization

Executed exactly once on power-up (first scan boot trigger). Clears the internal command and mode arrays, resets active indices, and clears all fault registers and completion flags, establishing a clean baseline state.

## Idle

The block remains idle until it detects a valid sequence start request (Command = 1) via a rising-edge trigger. No execution occurs if an active fault is latched.

## Asynchronous Parameter Validation

Prior to sequence execution, the block validates configuration parameters sequentially (one motor checking scan per plc loop). It validates that MotorCount is within limits (1..C_MaxMotors), and validates that configured modes (0..3) and commands (0..9) are valid. If any configuration fails validation, the state transitions directly to STATE_FAULT.

## Global Command Range Validation

The system Command input is continuously monitored in runtime. If the command value falls outside the valid range of 0 to 3 (0=Idle, 1=Start, 2=Abort, 3=Reset Fault), the block latches an Invalid System Command fault (FaultCode 109) and transitions immediately to STATE_FAULT (unless already in a fault state).

## Command Routing and Dispatching

Iterates through the motors. If a motor is in Manual Mode, processing is skipped. If a motor is in Bypass or Out Of Service, mode is assigned and feedback checking is bypassed. In Auto Mode, the operational commands are dispatched. If the command does not require feedback monitoring (e.g. Continue=7, Pause=8, HornOff=9), it advances immediately; otherwise, it waits for feedback.

## Feedback and Timeout Verification

Waits until the active motor feedback matches the requested command. It checks for invalid feedback status patterns (Ready, Running, and Fault all FALSE), checks for active motor faults, and supervises the execution using the MotorTimeout timer. Any validation failure triggers a system shutdown.

## Emergency Safe Shutdown & Fault Handling

If a global abort override (Command = 2) or a critical interlock permissive loss occurs, the block shifts to STATE_SAFE or STATE_FAULT. In these states, it commands all active motors to structurally stop (C_CmdStop) within bounds, and clears execution flags. Faults remain latched until an edge-triggered reset command is issued.

# 5. Operating Modes

Individual motor behavior is governed by the MotorModes index inputs:

| Value | Mode | Description |
| --- | --- | --- |
| 0 | Manual | Manual mode: loop skips command processing and feedback monitoring for this motor. |
| 1 | Auto | Auto mode: normal command routing and feedback status matching are enforced. |
| 2 | Out Of Service | OOS mode: assigns the out of service status and bypasses feedback monitoring. |
| 3 | Bypass | Bypass mode: assigns bypass status, bypasses feedback monitoring, allows maintenance/testing. |

# 6. Command Interface

The FB executes actions based on edge-triggered values on the Command input:

| Value | Command | Description |
| --- | --- | --- |
| 0 | None | No command or idle state. |
| 1 | Start | Sequence start trigger. Initiates validation and starting loop. |
| 2 | Abort | Global abort override. Forces immediate transition to STATE_SAFE, stopping all motors. |
| 3 | Reset Fault | Fault reset trigger. Clear active latched faults on rising edge. |

# 7. Input Signals

| Signal | Type | Description |
| --- | --- | --- |
| Command | WORD | Execution control command (0=Idle, 1=Start, 2=Abort, 3=Reset Fault). |
| Interlock | BOOL | Global group start permissive. Must be active for sequence execution. |
| MotorCount | UINT | Active number of motors defined in the loop (Range: 1..C_MaxMotors). |
| MotorTimeout | TIME | Feedback validation timer preset limit. |
| SequenceCommands | ArrayOfMotorWords | Target control commands configured per motor. |
| MotorModes | ArrayOfMotorWords | Operating mode configuration assigned per motor. |
| MotorStatusWords | ArrayOfMotorWords | Status feedback arrays transmitted back from individual motor blocks. |

# 8. Output Signals

| Signal | Type | Description |
| --- | --- | --- |
| MotorCommandWords | ArrayOfMotorWords | Output commands array mapped directly to individual motor control interfaces. |
| MotorModeWords | ArrayOfMotorWords | Output mode status array mapped to individual motor interfaces. |
| ActiveMotorIndex | UINT | Indicates the index of the motor currently being processed. |
| SequenceRunning | BOOL | Indicates sequence is actively running and executing commands. |
| SequenceComplete | BOOL | Execution completed flag. Latches TRUE for one scan at completion. |
| StatusWord | WORD | Packed bit register conveying state information (see Section 11). |
| FaultActive | BOOL | Latched general group fault flag. |
| FaultCode | UINT | Numeric diagnostic code indicating active fault details. |

# 9. State Machine

The sequence execution utilizes a structured state machine with the following states:

| State Constant | Numeric | Description |
| --- | --- | --- |
| STATE_IDLE | 0 | Awaiting rising edge of start command. |
| STATE_VALIDATE | 10 | Asynchronous validation check of configuration parameters (one motor per scan). |
| STATE_SEND_COMMAND | 20 | Routing modes and active command parameters to the current motor index. |
| STATE_WAIT_FEEDBACK | 30 | Evaluating status feedback word of active motor against command targets. |
| STATE_NEXT_MOTOR | 40 | Incrementing loop pointer safely to move to the next motor configuration. |
| STATE_COMPLETE | 50 | Final sequence completion scan. Sets completion flags, returns to IDLE. |
| STATE_SAFE | 90 | Clears run flags and forces stop commands on all active motor channels. |
| STATE_FAULT | 99 | Latched fault state. Clears run flags, stops motors, and awaits a reset trigger. |

# 10. Sequence of Operation

Power-up initialization clears buffers -> Idle -> Detect start edge (Command = 1) -> Enter STATE_VALIDATE: check MotorCount limits (1..C_MaxMotors) and validation parameters -> Enter STATE_SEND_COMMAND: assign modes, evaluate bypass/manual/auto routes -> If Auto: dispatch command, enter STATE_WAIT_FEEDBACK -> Check feedback match, status validation, and timeout limit -> Advance index in STATE_NEXT_MOTOR -> Repeat for all configured motor elements -> Complete execution in STATE_COMPLETE -> Reset to Idle.

# 11. StatusWord Definition

The StatusWord output register is packed dynamically at the end of every task execution:

| Bit | Name | Description |
| --- | --- | --- |
| 0 | Ready | System is idle and ready for commands (eState = STATE_IDLE and no active fault). |
| 1 | SequenceRunning | Group start sequence is actively executing. |
| 2 | SequenceComplete | Group start sequence completed successfully (pulsed for one cycle). |
| 3 | Interlock | Reflects the state of the physical Group Permissive Interlock input. |
| 4 | Safe Active | Reflects that the system is currently executing the safe shutdown sequence. |
| 5 | Wait Feedback | Sequence is currently waiting for feedback confirmation from a motor. |
| 6 | Start Command Active | Indicates the start command is currently active (Command = 1). |
| 15 | Fault Active | A latched system-level group fault is active. |

# 12. Fault Handling

Latched Faults: Fault Latching: Faults remain latched until a reset request is processed.

Reset Action: Fault Reset: Setting Command = 3 executes an edge-triggered clear. If the trigger condition persists, the fault re-latches immediately.

Safe Stops: Safe State Actions: Safe shutdown is executed automatically upon any critical fault. In STATE_FAULT or STATE_SAFE, the logic commands all active motor channels to stop.

Diagnostics: Diagnostics Checks: Real-time checks monitor for: invalid parameter limits, feedback timeout expirations, active motor error returns, lost permissives, and invalid feedback patterns.

# 13. Fault Code Table

| Fault Code | Name | Description | Operator Action |
| --- | --- | --- | --- |
| 101 | Invalid MotorCount | MotorCount is out of valid range (1..C_MaxMotors). | Check configuration and parameter bounds. |
| 102 | Interlock Lost | Permissive interlock dropped while sequence was executing. | Inspect safety circuits and loop interlock signals. |
| 103 | Motor Timeout | Motor failed to reach target feedback state within configured timeout. | Check motor mechanical path, controls, and sensor feedbacks. |
| 104 | Motor Fault Detected | Motor feedback status register indicates active fault (Bit 2 = 1). | Access active motor block diagnostic registers for detailed failure reason. |
| 105 | Invalid Sequence Command | Validation step detected an out-of-range command configuration (> 9). | Correct sequence commands array entries. |
| 106 | Invalid Motor Mode | Validation step detected an out-of-range mode configuration (> 3). | Correct motor modes array entries. |
| 108 | Invalid Motor Status | Active motor status word feedback exhibits invalid pattern (Ready, Running, and Fault all FALSE). | Verify motor node control power, communication, and wiring. |
| 109 | Invalid System Command | Global Command input register exceeds boundaries (not 0..3). | Check system Command source signals (HMI or sequence scheduler). |

# 14. Timing Diagram

Sequence Timing and Feedback Verification Pattern:

Command (Start) ____¦¯¯¯¯¦______________________________________ Seq Running ______¦¯¯¯¯¯¯¯¯¯¯¯¯¯¯¯¯¯¯¯¯¯¯¯¯¯¯¯¯¯¯¯¯¯¦_______ Active Index ======< Mtr 1 >< Mtr 2 >...< Mtr N >============ Motor 1 Cmd ______¦¯¯¯¯¯¯¯¯¦________________________________ Motor 1 Fbk __________¦¯¯¯¯¦________________________________ Motor 2 Cmd _______________¦¯¯¯¯¯¯¯¯¦_______________________ Motor 2 Fbk ____________________¦¯¯¯¦_______________________ Seq Complete ________________________________________¦¯¦_____

# 15. FBD Example

Functional Block Diagram interface block:

+---------------------------------------------+ ¦ FB_GroupStartControl ¦ Command --¦ Command MotorCommandWords¦-- ArrayOfMotorWords Interlock--¦ Interlock MotorModeWords¦-- ArrayOfMotorWords MtrCount --¦ MotorCount ActiveMotorIndex¦-- Index MtrTime --¦ MotorTimeout SequenceRunning¦-- Running SeqCmds --¦ SequenceCommands SequenceComplete¦-- Complete MtrModes --¦ MotorModes StatusWord¦-- Status MtrSts --¦ MotorStatusWords FaultActive¦-- Fault ¦ FaultCode¦-- Diagnostic +---------------------------------------------+

# 16. Structured Text Implementation

The complete Structured Text definition and state machine source code:

(*============================================================================================ DATA TYPES (UDT) ============================================================================================*) TYPE UDT_GroupStartLineState : ( STATE_IDLE := 0, STATE_VALIDATE := 10, STATE_SEND_COMMAND := 20, STATE_WAIT_FEEDBACK := 30, STATE_NEXT_MOTOR := 40, STATE_COMPLETE := 50, STATE_SAFE := 90, STATE_FAULT := 99 ); END_TYPE TYPE ArrayOfMotorWords : ARRAY[1..32] OF WORD; // Supports up to 32 motors. If the maximum number of motors changes, update this array size before recompiling. END_TYPE (*============================================================================================ FUNCTION_BLOCK FB_GroupStartControl ============================================================================================*) FUNCTION_BLOCK FB_GroupStartControl VAR_INPUT Command : WORD; Interlock : BOOL; MotorCount : UINT; MotorTimeout : TIME; SequenceCommands : ArrayOfMotorWords; MotorModes : ArrayOfMotorWords; MotorStatusWords : ArrayOfMotorWords; END_VAR VAR_OUTPUT MotorCommandWords : ArrayOfMotorWords; MotorModeWords : ArrayOfMotorWords; ActiveMotorIndex : UINT; SequenceRunning : BOOL; SequenceComplete : BOOL; StatusWord : WORD; FaultActive : BOOL; FaultCode : UINT; END_VAR VAR_CONSTANT C_MaxMotors : UINT := 32; (* Master Safe Commands *) C_CmdNoCommand : WORD := 0; C_CmdStop : WORD := 2; END_VAR VAR eState : UDT_GroupStartLineState := STATE_IDLE; bInitialized : BOOL := FALSE; bSafeStateRequested : BOOL; fbStartTrigger : R_TRIG; fbResetTrigger : R_TRIG; bTargetRunningState : BOOL; bTargetFaultState : BOOL; bFeedbackMatch : BOOL; idx : UINT; uiValidationIndex : UINT; InternalCommandWords : ArrayOfMotorWords; InternalModeWords : ArrayOfMotorWords; tonTimeoutTimer : TON; END_VAR (*============================================================================================ 1. POWER-UP INITIALIZATION (Executed exactly once on cold start) ============================================================================================*) IF NOT bInitialized THEN FOR idx := 1 TO C_MaxMotors DO InternalCommandWords[idx] := C_CmdNoCommand; InternalModeWords[idx] := 0; END_FOR; ActiveMotorIndex := 0; uiValidationIndex := 1; SequenceRunning := FALSE; SequenceComplete := FALSE; FaultActive := FALSE; FaultCode := 0; StatusWord := 16#0000; bSafeStateRequested := FALSE; eState := STATE_IDLE; bInitialized := TRUE; END_IF; (*============================================================================================ 2. EDGE DETECTION AND TIMER EXECUTION ============================================================================================*) fbStartTrigger(CLK := (Command = 1)); fbResetTrigger(CLK := (Command = 3)); tonTimeoutTimer( IN := (eState = STATE_WAIT_FEEDBACK), PT := MotorTimeout ); (*============================================================================================ 3. SYSTEM INTERLOCK AND GLOBAL ABORT MONITORING (Deterministic & Synchronous) ============================================================================================*) (* Global Command Range Validation *) IF (Command < 0) OR (Command > 3) THEN IF (eState <> STATE_FAULT) THEN FaultActive := TRUE; FaultCode := 109; (* Invalid System Command *) eState := STATE_FAULT; END_IF; END_IF; (* Operator Global Abort Override - Routes through STATE_SAFE *) IF (Command = 2) AND (eState <> STATE_FAULT) AND (eState <> STATE_SAFE) THEN eState := STATE_SAFE; END_IF; (* Critical Hardware Interlock Drop *) IF NOT Interlock AND SequenceRunning AND (eState <> STATE_FAULT) THEN FaultActive := TRUE; FaultCode := 102; (* Interlock Lost *) eState := STATE_FAULT; END_IF; (*============================================================================================ 4. DETERMINISTIC STATE MACHINE ENVIRONMENT ============================================================================================*) CASE eState OF STATE_IDLE: // 0: Waiting for valid execution request SequenceRunning := FALSE; ActiveMotorIndex := 0; uiValidationIndex := 1; (* Reset asynchronous verification pointer *) (* Evaluate Execution Rising Edge Request *) IF fbStartTrigger.Q AND NOT FaultActive THEN SequenceComplete := FALSE; (* Clear complete flag immediately upon new execution cycle *) SequenceRunning := TRUE; eState := STATE_VALIDATE; END_IF; STATE_VALIDATE: // 10: Asynchronous configuration check (One motor per scan) (* 4.1 Validate Total System Boundaries *) IF (MotorCount < 1) OR (MotorCount > C_MaxMotors) THEN FaultActive := TRUE; FaultCode := 101; (* Invalid MotorCount *) eState := STATE_FAULT; (* 4.2 Validate Current Motor Vector Parameters (No runtime loops) *) ELSIF (uiValidationIndex <= MotorCount) THEN (* Check Operational Modes Range Limits *) IF (MotorModes[uiValidationIndex] > 3) THEN FaultActive := TRUE; FaultCode := 106; (* Invalid Motor Mode *) eState := STATE_FAULT; (* Check Configured Command Spectrum Limits *) ELSIF (SequenceCommands[uiValidationIndex] > 9) THEN FaultActive := TRUE; FaultCode := 105; (* Invalid Sequence Command *) eState := STATE_FAULT; ELSE (* Motor is structurally valid, increment checking index for the NEXT scan *) uiValidationIndex := uiValidationIndex + 1; END_IF; (* 4.3 Validation Matrix Complete - Initialize Sequence Iteration *) ELSE ActiveMotorIndex := 1; eState := STATE_SEND_COMMAND; END_IF; STATE_SEND_COMMAND: // 20: Command routing assignments (* Check Array Boundary Termination Limit *) IF (ActiveMotorIndex > MotorCount) THEN eState := STATE_COMPLETE; ELSE (* Evaluate Current Motor Control Mode *) CASE TO_UINT(MotorModes[ActiveMotorIndex]) OF 0: (* Manual Mode: Completely skip processing *) eState := STATE_NEXT_MOTOR; 2, 3: (* Out of Service / Bypass Mode: Assign Mode, Bypass Step Monitoring *) InternalModeWords[ActiveMotorIndex] := MotorModes[ActiveMotorIndex]; eState := STATE_NEXT_MOTOR; 1: (* Auto Mode: Route Operational Commands *) InternalModeWords[ActiveMotorIndex] := MotorModes[ActiveMotorIndex]; (* Evaluate and apply explicit sequence command profile *) IF (SequenceCommands[ActiveMotorIndex] = 7) OR (* Continue *) (SequenceCommands[ActiveMotorIndex] = 8) OR (* Pause *) (SequenceCommands[ActiveMotorIndex] = 9) THEN (* HornOff *) (* Non-monitored commands pass automatically to the next element *) eState := STATE_NEXT_MOTOR; ELSE (* Write operational command to internal mirror EXACTLY ONCE *) InternalCommandWords[ActiveMotorIndex] := SequenceCommands[ActiveMotorIndex]; eState := STATE_WAIT_FEEDBACK; END_IF; END_CASE; END_IF; STATE_WAIT_FEEDBACK: // 30: Wait until requested command is achieved (* Dynamically isolate bit elements using standard IEC bit-slice syntax *) bTargetFaultState := MotorStatusWords[ActiveMotorIndex].%X2; (* Bit 2: Fault *) bTargetRunningState := MotorStatusWords[ActiveMotorIndex].%X1; (* Bit 1: Running *) (* 1. Structural Diagnostic Exception Check: Invalid Status Pattern Detection *) IF NOT MotorStatusWords[ActiveMotorIndex].%X0 AND NOT bTargetRunningState AND NOT bTargetFaultState THEN FaultActive := TRUE; FaultCode := 108; (* Invalid Motor Status (Ready=0, Running=0, Fault=0) *) eState := STATE_FAULT; (* 2. Detect Component Fault Traps *) ELSIF bTargetFaultState THEN FaultActive := TRUE; FaultCode := 104; (* Motor Fault Detected *) eState := STATE_FAULT; (* 3. Check for Timeout *) ELSIF tonTimeoutTimer.Q THEN FaultActive := TRUE; FaultCode := 103; (* Motor Timeout *) eState := STATE_FAULT; (* 4. Process Synchronous Command Status Verification Matrix *) ELSE bFeedbackMatch := FALSE; CASE TO_UINT(InternalCommandWords[ActiveMotorIndex]) OF 1, 4: (* Start Motor / Line Start: Expect Running *) IF bTargetRunningState THEN bFeedbackMatch := TRUE; END_IF; 2, 5, 6: (* Stop / Line Stop / Immediate Stop: Expect Not Running *) IF NOT bTargetRunningState THEN bFeedbackMatch := TRUE; END_IF; 3: (* Fault Reset: Expect Fault Clear *) IF NOT bTargetFaultState THEN bFeedbackMatch := TRUE; END_IF; END_CASE; (* Clean transition step to pointer alteration *) IF bFeedbackMatch THEN eState := STATE_NEXT_MOTOR; END_IF; END_IF; STATE_NEXT_MOTOR: // 40: Increment array pointer safely (One motor per scan) ActiveMotorIndex := ActiveMotorIndex + 1; eState := STATE_SEND_COMMAND; STATE_COMPLETE: // 50: Sequence fully executed SequenceComplete := TRUE; SequenceRunning := FALSE; ActiveMotorIndex := 0; eState := STATE_IDLE; STATE_SAFE: // 90: Clear runtime execution flags and flag safe output assignment SequenceRunning := FALSE; SequenceComplete := FALSE; ActiveMotorIndex := 0; bSafeStateRequested := TRUE; (* Triggers structured bounded cleanup in section 5 *) eState := STATE_IDLE; STATE_FAULT: // 99: Latched safe-failure holding block SequenceRunning := FALSE; ActiveMotorIndex := 0; bSafeStateRequested := TRUE; (* Monitor Edge Detection for System Fault Clearing *) IF fbResetTrigger.Q THEN FaultActive := FALSE; FaultCode := 0; eState := STATE_IDLE; END_IF; END_CASE; (*============================================================================================ 5. OUTPUT TERMINAL ASSIGNMENT (One clean loop execution restricted strictly to active bounds) ============================================================================================*) IF bSafeStateRequested THEN (* Process ONLY the active motor count payload zone *) IF (MotorCount >= 1) AND (MotorCount <= C_MaxMotors) THEN FOR idx := 1 TO MotorCount DO InternalCommandWords[idx] := C_CmdStop; END_FOR; ELSE (* Ultimate execution fallback bounds protection if MotorCount itself is invalid *) FOR idx := 1 TO C_MaxMotors DO InternalCommandWords[idx] := C_CmdStop; END_FOR; END_IF; bSafeStateRequested := FALSE; (* Acknowledge and clear request trigger *) END_IF; (* Final Structural Output Boundary Copies *) MotorCommandWords := InternalCommandWords; MotorModeWords := InternalModeWords; (*============================================================================================ 6. STATUS WORD PACKING ============================================================================================*) StatusWord := 16#0000; StatusWord.%X0 := (eState = STATE_IDLE) AND NOT FaultActive; StatusWord.%X1 := SequenceRunning; StatusWord.%X2 := SequenceComplete; StatusWord.%X3 := Interlock; StatusWord.%X4 := (eState = STATE_SAFE); (* Point 12: Clear semantic mapping directly to State *) StatusWord.%X5 := (eState = STATE_WAIT_FEEDBACK); StatusWord.%X6 := (Command = 1); StatusWord.%X15 := FaultActive;

# 17. Design Rules

One assignment per physical output channel to avoid race conditions.

Strict state machine architecture to control sequence steps deterministically.

Active faults are latched and require an explicit Reset command to clear.

Control commands (Start, Reset) are edge-triggered to avoid HMI continuous high lockouts.

Structured loops process only within active MotorCount bounds to protect memory limits.

Safe state transitions automatically on interlock drops, command aborts, or faults.

Feedback timeout timers are executed on every task scan to avoid scan-invariance issues.

Centralized UDT array declarations (ArrayOfMotorWords) to support easy scaling of the physical motor count.

# 18. Assumptions

The physical system supports up to C_MaxMotors configuration (defined by UDT ArrayOfMotorWords size, default 32).

The sequence command and mode configurations match the indices of active motor status words.

The feedback timeout period (MotorTimeout) is configured appropriately for all motor units.

Motor stop command (C_CmdStop = 2) is a safe command that halts motor motion.

# 19. Future Enhancements

Dynamic individual motor timeout configurations instead of a single group timeout.

Simulation mode for dry run testing of the sequence without physical IO.

Enhanced alarm history mapping for identifying specific motor failure details directly in the StatusWord.

Support for parallel Stop blocks within the sequence.

# 20. Revision History

| Version | Date | Author | Description |
| --- | --- | --- | --- |
| V1.0 | 09-Jul-2026 | Vijayakumar V S | Initial draft of FB_ GroupStartControl specification. |